## F2.2
Adani Power Ltd.
MYT Petition Formats - Generation
Form 2.2: Energy Charges for Thermal Generation
Adani Dahanu Thermal Power Station
Sr. No. | Particulars | Units | FY 2024-25 |  |  |  | Remarks
|  |  | Apr-Aug (Prov. Actual with normative parameters) | Sept-Mar (Estimated) | April - March (Estimated) | Revised
|  |  | (h) | (i) | (j) = (h) + (i)
1 | Operational Parameters
1.1 | Total Capacity | MW | 500 | 500 | 500 | 500
1.2 | Target Availability for full recovery of AFC | % | 85 | 85 | 85 | 85
1.2.1 | In High Demand Season | %
| Peak Hours | %
| Off-Peak Hours | %
1.2.2 | In Low Demand Season | %
| Peak Hours | %
| Off-Peak Hours | %
1.3 | Actual/Projected Availability | % | 90.02% | 88.21% | 88.97% | 88.97%
1.4 | Target PLF for Incentive | %
1.5 | Actual/Projected PLF | % | 75.44% | 75% | 75.18% | 75.18%
1.6 | Scheduled Generation | MU
1.7 | Actual/Projected Gross Generation | MU | 1385.094 | 1908 | 3293.094 | 3293.094
1.8 | Normative Auxiliary Energy Consumption | %
| Normative Auxiliary Energy Consumption (Excluding FGD) |  | 8.5 | 8.5 | 8.5 | 8.5
| Actual Auxiliary Energy Consumption (FGD) |  | 1.2 | 1.2 | 1.2 | 1.2
1.9 | Actual/Projected Auxiliary Energy Consumption | % | 9.7% | 9.7% | 9.7% | 9.7%
1.1 | Actual/Projected Auxiliary Energy Consumption | MU | 134.3541 | 185.076 | 319.4301 | 319.4301
1.11 | Actual/Projected Net Generation | MU | 1250.7399 | 1722.924 | 2973.6639 | 2973.6639
1.12 | Normative Gross Station Heat Rate | kcal/kWh | 2430 | 2430 | 2430 | 2430
1.13 | Actual/Projected Gross Station Heat Rate | kcal/kWh | 2430 | 2430 | 2430 | 2430
1.14 | Normative Secondary Fuel Oil Consumption | ml/kWh | 0.5 | 0.5 | 0.5 | 0.5
1.15 | Actual/Projected Secondary Fuel Oil Consumption | ml/kWh | 0.5 | 0.5 | 0.5 | 0.5
1.16 | Normative Transit Loss | % | 0.8% / 0.2% | 0.8% / 0.2% | 0.8% / 0.2% | 0.8% / 0.2%
1.17 | Actual/Projected Transit Loss | %
2 | Fuel Parameters (for each primary and secondary fuel)
2.1 | Calorific Value (As billed) | kcal/kg | 3743.3645 | 3687.4476 | 3710.175 | 3713.0822
2.1.1 | Fuel 1 - Domestic Coal | kcal/kg | 3637.4628 | 3714 | 3637.4628 | 3637.4628
2.1.2 | Fuel 2 - Imported Coal | kcal/kg | 4491 | 4491 | 4491 | 4491
2.1.3 | Fuel 3 - Raw Coal |  | 3754.4605 | 3669.8174 | 3700.4492 | 3700.4492
2.1.4 | Fuel 4 - Addnl. Raw coal
2.1.5 | LDO | kcal/kg | 10704.6515 | 10690.3631 | 10696.3729 | 10696.3729
2.2 | Calorific Value (As received) | kcal/kg | 3215.2827 | 3047.0229 | 3115.4122 | 3119.9595
2.2.1 | Fuel 1 - Domestic Coal | kcal/kg | 3645.0667 | 3714 | 3645.0667 | 3645.0667
2.2.2 | Fuel 2 - Imported Coal | kcal/kg | 4287 | 4287 | 4287 | 4287
2.2.3 | Fuel 3 - Raw Coal |  | 3104.4605 | 3019.8174 | 3050.4492 | 3050.4492
2.2.4 | Fuel 4 - Addnl. Raw coal
2.2.5 | LDO | kcal/kg | 10704.6515 | 10690.3631 | 10696.3729 | 10696.3729
2.3 | GCV loss in transit |  | 528.0817 | 640.4247 | 594.7629 | 593.1227
2.3.1 | Fuel 1 - Domestic Coal |  | -7.6039 | 0 | -7.6039 | -7.6039
2.3.2 | Fuel 2 - Imported Coal |  | 204 | 204 | 204 | 204
2.3.3 | Fuel 3 - Raw Coal |  | 650 | 650 | 650 | 650
2.3.4 | Fuel 4 - Addnl. Raw coal
2.3.5 | LDO |  | 0 | 0 | 0 | 0
2.5 | Calorific Value (As Fired) | kcal/kg | 3102.9536 | 2832.0289 | 2942.1463 | 2946.7153
2.5.1 | Fuel 1 - Domestic Coal | kcal/kg | 3788.7977 | 3669.7615 | 3788.7977 | 3788.7977
2.5.2 | Fuel 2 - Imported Coal | kcal/kg | 4095 | 4095 | 4095 | 4095
2.5.3 | Fuel 3 - Raw Coal |  | 2937.6128 | 2804.3189 | 2852.5571 | 2852.5571
2.5.4 | Fuel 4 - Addnl. Raw coal
2.5.5 | LDO | kcal/kg | 10704.6515 | 10690.3631 | 10696.3729 | 10696.3729
2.6 | Actual stacking loss | kcal/kg | 112.3291 | 120 | 120 | 120
2.6.1 | Fuel 1 - Domestic Coal | kcal/kg | -143.731 | 44.2385 | -143.731 | -143.731
2.6.2 | Fuel 2 - Imported Coal | kcal/kg | 192 | 192 | 192 | 192
2.6.3 | Fuel 3 - Raw Coal |  | 166.8477 | 215.4985 | 197.8921 | 197.8921
2.6.4 | Fuel 4 - Addnl. Raw coal
2.6.5 | LDO | kcal/kg | 0 | 0 | 0 | 0
2.7 | Landed Fuel Price per unit | Rs/MT | 5019.1419 | 4943.1641 | 4974.0453 | 4990.2647
2.7.1 | Fuel 1 - Domestic Coal | Rs/MT | 5369.3308 | 5553.2557 | 5369.3308 | 5369.3308
2.7.2 | Fuel 2 - Imported Coal | Rs/MT | 9268.4143 | 9268.4143 | 9268.4143 | 9268.4143
2.7.3 | Fuel 3 - Raw Coal |  | 4874.7473 | 4848.2666 | 4857.8498 | 4857.8498
2.7.4 | Fuel 4 - Addnl. Raw coal |  |  |  |  | 0
2.7.5 | LDO | Rs/KL | 73497.5562 | 73240.2722 | 73348.4873 | 73348.4873
3 | Fuel Consumption and Heat Contribution (for each fuel separately)
3.1 | Specific Fuel Consumption | kg/kWh | 0.7816 | 0.82858 | 0.80966 | 0.80844
3.1.1 | Fuel 1 - Domestic Coal | kg/kWh | 0.13802 | 0 | 0.058114 | 0.058026
3.1.2 | Fuel 2 - Imported Coal | kg/kWh | 0.01015 | 0.017789 | 0.014591 | 0.017542
3.1.3 | Fuel 3 - Raw Coal |  | 0.63343 | 0.81079 | 0.73696 | 0.73287
3.1.4 | Fuel 4 - Addnl. Raw coal
3.1.5 | LDO | ml/kWh | 0.5 | 0.5 | 0.5 | 0.5
3.2 | Total Fuel Consumption | MT | 1082590.3998 | 1580933.4345 | 2663523.8343 | 2662254.6884
3.2.1 | Fuel 1 - Domestic Coal | MT | 191175.0439 | 0 | 191175.0439 | 191083.9507
3.2.2 | Fuel 2 - Imported Coal | MT | 14058.4506 | 33941.5494 | 48000 | 57767.2798
3.2.3 | Fuel 3 - Raw Coal |  | 877356.9052 | 1546991.8851 | 2424348.7903 | 2413403.4579
3.2.4 | Fuel 4 - Addnl. Raw coal
3.2.5 | LDO | KL | 692.547 | 954 | 1646.547 | 2600.547
3.3 | Heat Content (each fuel separately) | Million kcal | 2425.2706 | 2425.2769 | 2425.2743 | 2425.2743
3.3.1 | Fuel 1 - Domestic Coal | Million kcal | 522.9418 | 0 | 224.1675 | 223.8199
3.3.2 | Fuel 2 - Imported Coal | Million kcal | 41.5635 | 75.2897 | 60.8324 | 73.1322
3.3.3 | Fuel 3 - Raw Coal |  | 1860.7653 | 2349.9872 | 2140.2744 | 2128.3221
3.3.4 | Fuel 4 - Addnl. Raw coal
3.3.5 | LDO | Million kcal | 4.7294 | 4.7231 | 4.7257 | 4.7257
| Total Heat Content | Million kcal | 2430 | 2430 | 2430 | 2430
4 | Total Fuel Cost
4.1.1 | Fuel 1 - Domestic Coal | Rs Crore | 102.6482 | 0 | 102.6482 | 102.5993
4.1.2 | Fuel 2 - Imported Coal | Rs Crore | 13.03 | 31.4584 | 44.4884 | 53.5411
4.1.3 | Fuel 3 - Raw Coal |  | 427.6893 | 750.0229 | 1177.7122 | 1172.3952
4.1.4 | Fuel 4 - Addnl. Raw coal
4.1.5 | LDO | Rs Crore | 5.0901 | 6.9871 | 12.0772 | 19.0746
| Total Fuel Cost | Rs Crore | 548.4575 | 788.4685 | 1336.926 | 1347.6102
5 | Other Charges and Adjustments
5.1.1 | Other Charges (pl. specify details) | Rs Crore | 0 | 0 | 0 | 0
5.1.2 | Other Adjustments (pl. specify details)- PLF incentive | Rs Crore | 0 | 0 | 0 | 0
| Total Other Charges and Adjustments | Rs Crore | 0 | 0 | 0 | 0
6 | Total Cost (4+5) | Rs Crore | 548.4575 | 788.4685 | 1336.926 | 1347.6102
7 | Energy Charge per unit (ex-bus) (6/1.11) | Rs/kWh | 4.3851 | 4.5763 | 4.4959 | 4.5318
DISCOM Scheduled generation
* - In case MTR Order is yet to be issued, then MYT Order values to be captured under this column |  |  | 1867.7955 | 2054.0047 | 1973.319
|  |  | 17.66% | 0% | 7.178% | 7.178%
Note |  |  | 1.299% | 2.147% | 1.802% | 2.17%
1 | Details to be submitted for each primary and secondary fuel separately |  | 81.04% | 97.85% | 91.02% | 90.65%
2 | The energy charge should be computed for open cycle operation and combined cycle operation separately in case of gas/liquid fuel fired plants.
3 | Operational data are to be submitted for each Unit of each station separately
[6 empty] | 4% | 2024-04-01
2024-10-15
[6 empty] | 2.17% | 198
Note on E20: ANUPAM PATRA: Actual till Aug 24
Note on E30: ANUPAM PATRA: Actual net generation till Aug 24